Leak Detection For Building Service Columns / CSI Model Specification

TraceTek® Zone Leak Detection and Location System with Touch Screen Control Panel

Part 1 – General

1.1	Furnish a complete leak detection system including electronic alarm modules, water sensing cable, graphic display map, and auxiliary equipment. The system shall be capable of automatically detecting the presence of water at any point along the continuous length of sensing cable. The system shall sound an alarm and display the location point of liquid contact within .1% of the total connected sensing cable length. No more than one foot of liquid, in contact with a sensing cable at a depth of 1/16 inch, shall be required to cause an audible alarm at the electronic alarm module.

The system shall be UL listed, FM approved, and CSA certified. The system manufacturer shall have at least five years of experience with leak detection and location technology, including both sensing cable and the associated alarm electronics. The manufacturer shall provide written verification of current ISO 9001 registration.

1.2	The system shall be manufactured by Pentair Thermal Management, TraceTek Products Group, Menlo Park, California, distributed by California Detection Systems, Inc. (714) 692-0015.

Part 2 -Products

2.1	The alarm and locating module (Model TT-TS12) shall be housed in a NEMA 12 enclosure and have a 12” full color, high resolution SVGA display with touch screen, which provides status and alarm data. It shall be capable of monitoring up to 250 external TraceTek leak detection circuits. The alarm and locating module shall continuously monitor all sensing cable for liquid contact. Contact with liquid shall result in an audible alarm, display of the leak location with the name of the reporting channel and the distance along the cable in feet or meters. The leak location information is also used to position a flashing “LEAK” icon over a user designated background image.

The electronic alarm module shall continue to monitor the sensing cable after detection of liquid. It shall re-alarm if the liquid spreads, or if a second leak is detected, more than a specified distance from the original location.

The electronic alarm module shall provide multi-level password protection.

Startup is automatic and should there be a power disruption, the system will pick up where it left off including the re-flashing of any working alarms that have not been cleared or that occurred during the power outage.

The electronic alarm module shall have onboard event history for up to 5,000 events stored in a non-volatile memory. All event history can be downloaded to a USB memory stick in XML format.

The alarm module shall provide a built in Modbus RTU serial interface with user adjustable baud rates and port setup. Modbus/TCP is supported via one of two Ethernet connectors.

2.2	The sensing cables shall detect the presence of the type of liquid for which the cable was designed. The cable shall be constructed with no metal parts exposed to the environment.

The aqueous chemical sensing cable (TT3000) shall be resistant to corrosion. It shall detect the presence of water and other aqueous chemicals, but shall not detect fuels. The sensing cable shall be constructed of two sensor wires and two insulated wires embedded in a fluoropolymer carrier rod. The sensor wires shall be jacketed with conductive fluoropolymer.

The hydrocarbon sensing cable (TT5000) shall detect the presence of diesel, gasoline, jet fuel, and other hydrocarbons but shall not detect water. The sensing cable shall consist of a four-wire core, conductive jacket, and polymer over-braid. The core shall consist of two sensor wires and two insulated wires. The sensor wires shall be jacketed with a conductive polymer. The fuel sensor shall be replaced after exposure to hydrocarbons.

The sensing cables shall be capable of accommodating any number of branches using TraceTek branching connectors (TT -OZC-MC).

2.3	Jumper cable shall be available to interconnect sensing cables or to facilitate remote mounting of the electronic alarm module.

2.4	A TraceTek portable test box (TT-PTB-1000) shall be provided to the leak detection system installer. It shall become the property of the owner, upon system acceptance, for use in the ongoing preventive maintenance of the leak detection system.

Part 3 -Execution

3.1	All TraceTek system components shall be installed in accordance with the manufacturer's installation instructions. The sensing cable installer shall be responsible for installation of the sensing cable, functional testing, and mapping of the system.  Tyco Thermal Controls or its trained local representative shall provide supervision and training.

3.2	The 5 foot long sensing cables shall be installed around the base of the vertical service column pipe(s), on each floor. Sensing cable shall be secured with plastic hold-down clips (TT-HDC-1/4).

3.3	Upon completion of the system installation, the zone cable farthest from the alarm module shall be immersed in approximately 1 foot of the appropriate liquid to be detected, at a depth of 1/8 inch, to confirm that an audible alarm is generated at the alarm module and that the appropriate zone number is indicated on the electronic alarm module. The installer shall perform and certify the tests in the presence of the owner’s representative.

3.4	A graphic display map prepared from "as built" drawings shall be furnished upon completion. The map shall indicate the location of each sensing cable, landmarks such as equipment, change of cable direction, and it’s zone number, per the manufacturer’s instructions. The map shall be mounted next to the alarm and locating module.